## Sheet1
Function under test | Panel Type | Comments/Fault description | Old Tools Comparison (If applicable) | Fault Replication process
Booting up the tools/Default state of the tools | 16,32 | Tools open up to CAST PROTOCOL 1 LOOP by default, They also have Send to panel, auto adjust DST and blink polling LED in site config ticked as standard on start-up. | The old version of XFP tools and the current version of ZFP tools open to the apollo protocol.
Closing Down tools |  | Close down correctly, no crashing on closing down the tools.
Sending the default state to the panel | 16 Zone | A pop up box (Uploading system to panel) will appear when send to panel is selected, this option doesn’t open in the center and is off at the 5 o'clock position on the screen. This pop up when pressed opens up another identical box immediately after pressing which also requires accepting before the tools will send to the panel. The time and date also sends over correctly. |  | Click send System to panel > Popup box will open (click accept) > popup box will open (click accept again) > tools will send to panel
Receiveing Data from the panel | 16, 32 | The panel sends over devices,groups and zone correctly. However the cause and effect sent by a factory default panel and shown on the tools is Sounder Evac and in the next row Sounder alert. These usually have a group (by default its normall all groups) to action on. a Cause which is in the Occurs when column (such as zone or panel in fire) and a reset actionable (such as reset when panel reset). but in the tools its just the first box that has data (Sounder evac) |  | The image at the top shows how it looks after a download from the panel The bottom image is how I think it should look, I could be wrong this may need to be confirmed by a 3rd party
Sending to the panel Progress Box issue | 16, 32 | The progress box when sending a System config to the panel is showing that it is sending Loop-2 devices instead of loop-1 device, I believe this is a naming error more than an actual fault. However, on my 1 loop panel the tools still send loop-2 devices. if possible could this be hidden or removed? Same issue with 32 zone 2 loop however the pop up box says its sending loops 2 and 3 instead.
Device details, loop 1-2 mismatch | 16 Zone | Device details and the loop tabs do not update eachother with device information, such as zone,groups or modes. If there is a mismatch on a device it will not function as was intended. For example if I have a device in group 2 on device details and havent changed it in loop 1 it will still be what it was orignally in the loop 1 tab, this then causes issues with the sounder groups as when i try to set the panel to only sound group 2 sounders it will instead set off all the sounders on the loop. |  | This fault is replicable and is much easier to explain with it in progress, come see tom if neccesary. Cannot recreate anymore but the fault still exists in 8.1.1
Receiveing panel cause and effects | 16,32 | Cause and effects are not being retreived from the panel correctly | Old Tools is receving the C&E correctly | See images for more information on fault On the 32 Zone XFP the tools receive the correct cause and effects,when it has no loop data to retreive. When it has loop data the cause and effects do not transfer correctly
Sending System to a 32 Zone, 2 Loop Panel | 32 Zone 2 loop | Sending a config from the tools to a 32 Zone panel causes the progress box to say it is sending loops 2 and loops 3, rather than loops 1 and 2 simmilar issue to one on the 16 Zone XFP |  | Send a config with 2 loops to a 32 zone panel to see the pop up box
Saving System config | 16,32 | Presave check will pop up if there are issues with the config, along with the data validation box. Saves as .xfp2
Loading System Config | 16,32 | Loads correctly with the same data that was saved previously.
Downloading Apollo config from panel to the tools | Apollo 1 loop | The tools do not correctly receive sounder groups on apollo and has them all as blank. |  | Cannnot recreate
Customer 1 | 16 Zone, Apollo, CAST | Tested customer 1's isssue and could not repeat the issue
Customer 2 | Apollo, CAST | Tested customer 2's issue and could not be repeated
Customer 3 | 16 Zone Apollo, CAST | Tested customer 3's issue and could not repeat the issue
Customer 4 | Apollo, CAST | Tested customer 4's issues and could not repeat it with tools version 8.1.1, the tools will open in whatever protocol was last used, in my case that was cast. The tools swapped from cast to apollo when the apollo box is ticked.
Customer 5 | Apollo, CAST | Tested Customer 5's issue and could not replicate the fault
Customer related fault | Apollo | I only had 1 issue when testing customer faults which was when I sent a config to the tools and then that same config back to the panel the panel had faults after the sending. Group 12 sounders had faults but this went away almost immediately, the next fault was loop 1 device 65 device missing (25) this too went away after 2-3 minutes after this i could not recreate this. TESTED ON APOLLO to match the customer faults.